## Instructions
CONCEALED SPRINKLER DATA COLLECTION PROJECT
The American Society for Health Care Engineering (ASHE) is actively gathering data on concealed fire sprinklers to enhance safety protocols. Concealed sprinklers, defined in NFPA 13, Standard for the Installation of Sprinkler Systems, and referenced in NFPA 25, Standard for the Inspection, Testing, and Maintenance of Water-Based Fire Protection Systems, are designed with a cover plate to aesthetically blend into the ceiling, making them less obtrusive. However, this design necessitates periodic inspection to ensure functionality and prevent premature activation. In 2022, the NFPA 25 committee proposed a five-year inspection interval to align with other maintenance activities requiring similar equipment, optimizing resource utilization. This initiative underscores the commitment to continuous improvement in safety measures, acknowledging the balance between thorough inspection processes and practical considerations of cost and effort for facility owners and inspectors. The technical committee's decision, despite some opposition, indicates a consensus on the importance of these inspections while also recognizing the need for a pragmatic approach to their implementation. ASHE requests your data so that we can help the committee develop a practical method for ensuring concealed fire sprinklers remain functional.
Step 1: | Verify inventory of backup sprinkler cover plate.
Note: Covers plates are specifically listed with approved sprinklers. Verify that a matching spare cover plate is available in case the plate is damaged during removal and needs to be replaced with a spare cover plate.
Step 2: | Have someone on standby at sprinkler valve in case sprinkler activates.
Note: Removing the cover plate should not result in sprinkler activation, but as a precaution, it is best to know the location of the sprinkler control valve and have someone standing by to operate the valve if necessary.
Step 3: | Inspect the cover plate to make sure it is not painted or caulked to the ceiling.
Note: It is not uncommon for a cover plate to inadvertently get painted or caulked to the drywall ceiling. If this is the case, the plate will need to be removed and replaced.
Step 4: | Remove cover plate by unscrewing.
Note: Some older sprinkler cover plates use other methods of attachment.
Step 5: | Observe sprinkler for any corrosion, significant dust accumulation or any other deficiency.
Note: Take a photo of any sprinklers that show signs of corrosion or other deficiency.
Step 6: | Record make, model and year of sprinkler.
Each sprinkler should have this information imprinted on the deflector or sometimes the arms of the sprinkler. Complete the information on the Form tab of this spreadsheet.
Step 7: | Where possible, reinstall the cover plate.
Note: If the cover plate is damaged or painted, replace with a new cover plate that is listed for use with the sprinkler.
Step 8: | Upload documentation.
Upload this form and any photos to:
Data Portal
If you have any questions, please contact:
Email ASHE Sprinkler Data Project

## Concealed Sprinklers
Photo references of different styles of concealed sprinklers
Painted Cover Plate

## Form
CONCEALED SPRINKLER INSPECTION FORM
Date | Facility Name/Building | Manufacturer | Model | Year of Mfg. | Condition of Cover Plate Acceptable? | Comments | Photo file name